## Výpočet výměníku
VÝPOČET VÝMĚNÍKU - 1. varianta (t11,t12,M1,t21,M2)
(pitná voda - invertovaný sirup 75 % suš.) | [5 empty] | t22 = ?
ZADANÉ HODNOTY
Typ výměníku: |  | CHS VT - 05
Sekce: | VLP - cvičný příklad ukazující vliv složení desek na parametry výměníku
(tlakové ztráty a teplosměnnou plochu při stejném tepelném výkonu)
|  |  |  | 1.varianta | 2.varianta
Médium 1 - ohřívané: |  |  |  | pitná voda | pitná voda
- teplota vstupní |  |  | t11 (oC) = | 15 | 15
- teplota výstupní |  |  | t12 (oC) = | 60 | 60
(zadaná hodnota - pro určení max. výkonu |  |  |  | 59.989 | 59.8503
zvoleného výměníku upravit na základě výsledků)
- průtočné množství |  |  | M1 (kg/h) = | 4000 | 4000
- max. příp. tlak. ztráty |  |  | dp1max (kPa) = | 100 | 100
- tloušťka inkrustací |  |  | s1i (mm) = | 0 | 0
- tep. vodivost inkr. |  |  | lambda1i (W/mK) = | 2 | 2
Médium 2 - ochlazované: |  |  |  | invert.sirup | invert.sirup
- teplota vstupní |  |  | t21 (oC) = | 80 | 80
- teplota vystupní |  |  | t22 (oC) = | 40 | 40
(odhad pro 1. iteraci - upravit na základě výsledků) |  |  |  | 39.75 | 39.82
- průtočné množství |  |  | M2 (kg/h) = | 7000 | 7000
- max. příp. tlak. ztráty |  |  | dp2max (kPa) = | 100 | 250
- tloušťka inkrustací |  |  | s2i (mm) = | 0.1 | 0.1
- tep. vodivost inkr. |  |  | lambda2i (W/mK) = | 2 | 2
Zapojení (souproud/protiproud): |  |  |  | protiproud | protiproud
Poznámka: |  | Vliv počtu paraleních kanálů a počtu chodů pro jednotlivé kapaliny
na velikost součinitele prostupu tepla, tlakové ztráty, velikost
a výkon výměníku
Var.1 - nízké tlakové ztráty; var.2 - zvýšené tlakové ztráty
Výpočet provedl: |  | P. Hoffman
Datum: |  | duben 2003
KONSTANTY VÝPOČTU
- mezera mezi deskami |  |  | s (mm) = | 4 | 4
- šířka kanálu |  |  | b (mm) = | 410 | 410
- délka kanálu |  |  | L (mm) = | 1240 | 1240
- ekvivalentní průměr kanálu |  |  | de (m) = | 0.0079227 | 0.0079227
- průtočný průřez kanálu |  |  | f (m2) = | 0.00164 | 0.00164
- teplosměnná plocha desky |  |  | A (m2) = | 0.437 | 0.437
- doporučená rychlost pro vodu a podobné roztoky 0,3 - 0,6 m/s (pro viskózní je <)
(rychlost upravit na základě vypočtených a přípustných tlakových ztrát)
- medium 1: |  | voda | w1dop (m/s) = | 0.4 | 0.4
- medium 2: |  | sirup | w2dop (m/s) = | 0.2 | 0.2
- vztahy pro výpočet fyzikálních vlastností
(vybrat z knihovny pro různá média - pro vodu se spočítá samo)
- max. příp. tlak v deskách |  |  | pmax (kPa) = | 1000 | 1000
- kritériální vztahy pro určení souč. prostupu tepla
a tlakových ztrát
(vybrat z knihovny pro různé desky)
- tloušťka desky |  |  | sd (mm) = | 1.3 | 1.3
- tepel. vodivost desky |  |  | lambdad (W/mK) = | 15 | 15
- hmotnost desky |  |  | Md (kg) = | 5.4 | 5.4
- hmotnost stojanu |  |  | Mst (kg) = | 200 | 200
(vybrat z knihovny pro různé desky)
- tepelné ztráty výměníku |  |  | z (%) = | 0 | 0
(v % předaného tepla)
VÝPOČET
1. Určení fyzikálních hodnot pro obě média
- Médium 1: |  |  |  | pitná voda | pitná voda
- střední teplota |  |  | t1s (oC) = | 37.5 | 37.5
- měrné teplo |  |  | c1 (kJ/kg.K) = | 4.1761 | 4.1761
- hmotnost |  |  | ro1 (kg/m3) = | 994.8571 | 994.8571
- souč. tep. vodivosti |  |  | lambda1 (W/m.K) = | 0.62404 | 0.62404
- dynamická viskozita |  |  | mi1 (Pa.s) = | 0.00068649 | 0.00068649
- kinematická viskozita |  |  | ni1 (m2/s) = | 6.9004e-07 | 6.9004e-07
- Prandtlovo číslo |  |  | Pr1 (-) = | 4.5229 | 4.5229
- Médium 2 (pro 1. iteraci): |  |  |  | invert.sirup | invert.sirup
- střední teplota |  |  | t2s (oC) = | 60 | 60
- měrné teplo |  |  | c2 (kJ/kg.K) = | 2.67 | 2.67
2. Tepelný výkon
Q1 = M1*c1*(t12-t11)/3600 |  |  | Q1 (kW) = | 208.8034 | 208.8034
Q2 = 100*Q1/(100-z); Q2´=M2*c2*(t21-t22) |  |  | Q2 (kW) = | 208.8034 | 208.8034
t22 = t21-(t12-t11)*M1*c1/(M2*c2) |  |  | Q2´ (kW) = | 207.6667 | 207.6667
1. iterace | 60 | 4.1858 | t22 (oC) = | 54.3452 | 54.3452 | 60 | 4.1858
2. iterace | 67.1726 | 4.1898 | t22 (oC) = | 54.3701 | 54.3701 | 67.1726 | 4.1898
3. iterace | 67.185 | 4.1898 | t22 (oC) = | 54.3701 | 54.3701 | 67.185 | 4.1898
4. iterace | 67.1851 | 4.1898 | t22 (oC) = | 54.3701 | 54.3701 | 67.1851 | 4.1898
5. iterace | 67.1851 | 4.1898 | t22 (oC) = | 54.3701 | 54.3701 | 67.1851 | 4.1898
- Médium 2 (pro vlastní výpočet): |  |  |  | invert.sirup | invert.sirup
- střední teplota |  |  | t2s (oC) = | 67.1851 | 67.1851
- měrné teplo |  |  | c2 (kJ/kg.K) = | 2.67 | 2.67
- hmotnost |  |  | ro2 (kg/m3) = | 1353 | 1353
- souč. tep. vodivosti |  |  | lambda2 (W/m.K) = | 0.391 | 0.391
- dynamická viskozita |  |  | mi2 (Pa.s) = | 0.025 | 0.025
- kinematická viskozita |  |  | ni2 (m2/s) = | 1.8477e-05 | 1.8477e-05
- Prandtlovo číslo |  |  | Pr2 (-) = | 170.7161 | 170.7161
3. Průtočné rychlosti médií
rychlost v případě průtoku pouze 1 mezideskovým kanálem
w1c = M1/(3600*ro1*f) |  |  | w1c (m/s) = | 0.68101 | 0.68101
w2c = M2/(3600*ro2*f) |  |  | w2c (m/s) = | 0.8763 | 0.8763
počet paralelních kanálů v 1 tahu - určeno ze zadaného widop
ppk1v = w1c/w1dop |  |  | ppk1v (-) = | 1.7025 | 1.7025
ppk2v = w2c/w2dop |  |  | ppk2v (-) = | 4.3815 | 4.3815
zvolený počet paralelních kanálů v 1 tahu
ppk1 |  | pitná voda | ppk1 (-) = | 3 | 2
ppk2 |  | invert.sirup | ppk2 (-) = | 6 | 2
rychlosti v mezideskových kanálech
w1 = M1/(3600*ro1*f*ppk1) |  |  | w1 (m/s) = | 0.227 | 0.3405
w2 = M2/(3600*ro2*f*ppk2) |  |  | w2 (m/s) = | 0.14605 | 0.43815
4. Určení součinitele prostupu tepla
Re1 = w1*de/ni1 |  |  | Re1 (-) = | 2606.3266 | 3909.4898
Nu1 = 0,0206*(Re1^0.916)*(Pr1^0.40)
|  |  | Nu1 (-) = | 50.7128 | 73.5219
alfa1 = Nu1*lambda1/de
|  |  | alfa1 (W/m2*K) = | 3994.4572 | 5791.0507
Re2 = w2*de/ni2 |  |  | Re2 (-) = | 62.623 | 187.869
Nu2 = 0,0206*(Re2^0.916)*(Pr2^0.40)
|  |  | Nu2 (-) = | 7.1217 | 19.4818
alfa2 = Nu2*lambda2/de
|  |  | alfa2 (W/m2*K) = | 351.4702 | 961.4609
k = 1/(1/alfa1+sd/lambdad+si1*0.001/lambdai1+si2*0.001/lambdai2+1/alfa2)
|  |  | k (W/m2*K) = | 309.3864 | 741.0532
5. Určení počtu desek ve výměníku (sekci)
dtlog = abs((t22-t11)-(t21-t12))/ln(abs((t22-t11)/(t21-t12)))
|  |  | dtlog (oC) = | 28.6001 | 28.6001
vypočtená teplosměnná plocha výměníku (sekce)
Aco = Q1*1000/(k*dtlog) |  |  | Aco (m2) = | 23.5977 | 9.8519
vypočtený počet desek ve vyměníku (sekci)
nco = Aco/A1 |  |  | nco (-) = | 53.9993 | 22.5445
vypočtený počet v serii zapojených tahů po ppk1 desek (kanálů) v jednotlivych tazich
pts1v = nco/(2*ppk1) |  |  | pts1v (-) = | 8.9999 | 5.6361
pts2v = nco/(2*ppk2) |  |  | pts2v (-) = | 4.4999 | 5.6361
zvolený počet v serii zapojených tahů po ppk2 desek (kanálů) v jednotlivych tazich
pts1 = nco/(2*ppk1) |  |  | pts1 (-) = | 11 | 7
pts2 = nco/(2*ppk2) |  |  | pts2 (-) = | 6 | 7
kontrola správnosti volby počtu paralelních kanálů a počtu tahů (chodů) - počty desek pd1
a pd2 se mohou lišit max. o 2 kusy (krajní kanály/desky), jinak musí mít některé tahy méně/více kanálů
(např. místo 6 x 6 = 36 dát 3 x 6 + 3 x 5 = 33) |  |  | pd1 (-) = | 33 | 14
|  |  | pd2 (-) = | 36 | 14
celkový počet desek ve výměníku (sekci)
pd = pts1*ppk1+pts2*ppk2+1 |  |  | pd (-) = | 70 | 29
Celková teplosměnná plocha výměníku (sekce)
Ac = (pd-1)*A1 |  |  | Ac (m2) = | 30.153 | 12.236
6. Kontrola tlakových ztrát
Médium 1 |  |  |  | pitná voda | pitná voda
Eu1 = 486*(Re1^-0.195)*(Pr1^-0.068)
|  |  | Eu1 (-) = | 94.6111 | 87.4187
tlakové ztráty na jedné desce (kanálu)
dp11 = Eu1*ro1*w1^2/1000 |  |  | dp11 (kPa) = | 4.8503 | 10.0835
celkové tlakové ztráty výměníku (sekce)
dp1c = pts1*dp11 |  |  | dp1c (kPa) = | 53.353 | 70.5844
max. přípustná tlak. ztráta |  |  | dp1max = | 100 | 100
Médium 2 |  |  |  | invert.sirup | invert.sirup
Eu2 = 486*(Re2^-0.195)*(Pr2^-0.068)
|  |  | Eu2 (-) = | 152.925 | 123.4354
tlakové ztráty na jedné desce (kanálu)
dp21 = Eu2*ro2*w2^2/1000 |  |  | dp21 (kPa) = | 4.4135 | 32.0616
celkové tlakové ztráty výměníku (sekce)
dp2c = pts2*dp21 |  |  | dp2c (kPa) = | 26.4809 | 224.4313
max. přípustná tlak. ztráta |  |  | dp2max = | 100 | 250
maximální přípustný tlak ve výměníku |  |  | pmax (kPa) = | 1000 | 1000
Pokud se tlakové ztráty podstatně liší od přípustných je nutno zvolit
vyšší nebo nižší počet paralelních kanálů v 1 tahu ppk1 nebo ppk2 a výpočet opakovat
NOVÝ VÝPOČET - určení max. ochlaz. 2.média t22 pro zvolené řazení výměníku
zvolený počet paralelních kanálů v 1 tahu (pro další výpočty, pokud nevyhovuje tlak. ztráta)
ppk1 |  | pitná voda | ppk1 (-) = | 3 | 2
ppk2 |  | invert.sirup | ppk2 (-) = | 6 | 2
rychlosti v jednotlivých tazích
w1 = M1/(3600*ro1*f*ppk1) |  |  | w1 (m/s) = | 0.227 | 0.3405
w2 = M2/(3600*ro2*f*ppk2) |  |  | w2 (m/s) = | 0.14605 | 0.43815
zvolený počet v serii zapojených tahů po ppk desek v jednotlivých tazích
pts1 = nco/(2*ppk1) |  |  | pts1 (-) = | 11 | 7
pts2 = nco/(2*ppk2) |  |  | pts2 (-) = | 6 | 7
kontrola správnosti volby počtu paralelních kanálů a počtu tahů (chodů) - počty desek pd1
a pd2 se mohou lišit max. o 2 kusy (krajní kanály/desky), jinak musí mít některé tahy méně/více kanálů
(např. místo 6 x 6 = 36 dát 3 x 6 + 3 x 5 = 33) |  |  | pd1 (-) = | 33 | 14
|  |  | pd2 (-) = | 36 | 14
celkový počet desek ve výměníku (sekci)
pd = pts1*ppk1+pts2*ppk2+1 = pd1+pd2+1 |  |  | pd (-) = | 70 | 29
Celková teplosměnná plocha výměníku (sekce)
Ac = (pd-1)*A1 |  |  | Ac (m2) = | 30.153 | 12.236
Určení součinitele prostupu tepla
Re1 = w1*de/ni1 |  |  | Re1 (-) = | 2606.3266 | 3909.4898
Nu1 = 0,0206*(Re1^0.916)*(Pr1^0.40)
|  |  | Nu1 (-) = | 151.7011 | 154.5996
alfa1 = Nu1*lambda1/de
|  |  | alfa1 (W/m2*K) = | 11948.9419 | 12177.2445
Re2 = w2*de/ni2 |  |  | Re2 (-) = | 62.623 | 187.869
Nu2 = 0,0206*(Re2^0.916)*(Pr2^0.40)
|  |  | Nu2 (-) = | 6.7626 | 18.4993
alfa2 = Nu2*lambda2/de
|  |  | alfa2 (W/m2*K) = | 333.7454 | 912.9738
k = 1/(1/alfa1+sd/lambdad+si1*0.001/lambdai1+si2*0.001/lambdai2+1/alfa2)
|  |  | k (W/m2*K) = | 310.8822 | 760.9721
Určení max. ochlazení média 2 (t22) ve výměníku (sekci) a ohřátí média 1 (t12)
odhad t22 pro i-tou iteraci - inv. sirup |  |  | t22i (°C) = | 39.75 | 39.82
vypočtená hodnota t22 |  |  | t22i+1 (°C) = | 39.7909 | 39.9149
odhad t12 pro i-tou iteraci - p. voda |  |  | t12i (°C) = | 60.04 | 59.95
vypočtená hodnota t12 |  |  | t12i+1 (°C) = | 59.989 | 59.8503
dtlog = abs((t22i-t11)-(t21-t12i))/ln(abs((t22i-t11)/(t21-t12i)))
|  |  | dtlog (oC) = | 22.2692 | 22.3502
Max. předané teplo ve výměníku
Qmax=k*Ac*dtlog |  |  | Qmax (kW) = | 208.7523 | 208.1087
Kontrola tepla předaného chl. vodě resp. odebranému sirupu
Q1 = M1*c1*(t12i-t11)/3600 |  |  | Q1 (kW) = | 208.7523 | 208.1087
Q2 = 100*Q1/(100-z) |  |  | Q2 (kW) = | 208.7523 | 208.1087
Q2´=M2*c2*(t21-t22i) |  |  | Q2´ (kW) = | 208.9646 | 208.6012
Teplota ochlazeného média 2 |  |  | t22i+1 (°C) = | 39.7909 | 39.9149
Teplota ohřátého média 1 |  |  | t12i+1 (°C) = | 59.989 | 59.8503
Kontrola tlakových ztrát
Médium 1
Eu1 = 486*(Re1^-0.195)*(Pr1^-0.068)
|  |  | Eu2 (-) = | 94.6111 | 87.4187
tlakové ztráty na jedné desce (kanálu)
dp11 = Eu1*ro1*w1^2/1000 |  |  | dp11 (kPa) = | 4.8503 | 10.0835
celkové tlakové ztráty výměníku (sekce)
dp1c = pts1*dp11 |  |  | dp1c (kPa) = | 53.353 | 70.5844
Médium 2
Eu2 = 486*(Re2^-0.195)*(Pr2^-0.068)
|  |  | Eu2 (-) = | 152.925 | 123.4354
tlakové ztráty na jedné desce (kanálu)
dp21 = Eu2*ro2*w2^2/1000 |  |  | dp21 (kPa) = | 4.4135 | 32.0616
celkové tlakové ztráty výměníku (sekce)
dp2c = pts2*dp21 |  |  | dp2c (kPa) = | 26.4809 | 224.4313
porovnání vypočtených a maximálních tlakových ztrát (kPa)
max. přípustná
|  |  | dp1max (kPa) = | 100 | 100
|  |  | dp2max (kPa) = | 100 | 250
maximální přípustný tlak ve výměníku (kPa)
|  |  | pmax (kPa) = | 1000 | 1000
Pokud jsou tlakové ztráty vyšši jak připustné je nutno zvolit vyšší počet paralelních
kanálů ppk1 nebo ppk2 a výpočet opakovat. Pokud jsou podstatně nižší je možno
snížit počet paralelních kanálů a výpočet opakovat s odpovídajícím zvýšení počtu tahů.
Pokud výsledky vyhovují možno spustit tisk.
Tisk vysledků
VÝPOČET VÝMĚNÍKU - 1. varianta (t11,t12,M1,t21,M2)
t22 = ?
ZADANÉ HODNOTY
Typ výměníku: | CHS VT - 05
Sekce: | VLP - cvičný příklad ukazující vliv složení desek na parametry výměníku
(tlakové ztráty a teplosměnnou plochu při stejném tepelném výkonu)
Poznámka: |  | Vliv počtu paraleních kanálů a počtu chodů pro jednotlivé kapaliny
na velikost součinitele prostupu tepla, tlakové ztráty, velikost
a výkon výměníku
Var.1 - nízké tlakové ztráty; var.2 - zvýšené tlakové ztráty
Výpočet provedl: |  | P. Hoffman
Datum: |  | duben 2003
|  |  |  | 1.varianta | 2.varianta
Zapojení: |  |  |  | protiproud | protiproud
Médium 1 - ohřívané: |  |  |  | pitná voda | pitná voda
- teplota vstupní |  |  | t11 (oC) = | 15 | 15
- vypočtená teplota výstupní |  |  | t12 (oC) = | 59.989 | 59.8503
- průtočné množství |  |  | M1 (kg/h) = | 4000 | 4000
- max. příp. tlak. ztráty |  |  | dp1max (kPa) = | 100 | 100
- tloušťka inkrustací |  |  | s1i (mm) = | 0 | 0
- tep. vodivost inkr. |  |  | lambda1i (W/mK) = | 2 | 2
Médium 2 - ochlazované: |  |  |  | invert.sirup | invert.sirup
- teplota vstupní |  |  | t21 (oC) = | 80 | 80
- teplota výstupní vypočtená |  |  | t22 (oC) = | 39.7909 | 39.9149
- průtočné množství |  |  | M2 (kg/h) = | 7000 | 7000
- max. příp. tlak. ztráty |  |  | dp2max (kPa) = | 100 | 250
- tloušťka inkrustací |  |  | s2i (mm) = | 0.1 | 0.1
- tep. vodivost inkr. |  |  | lambda2i (W/mK) = | 2 | 2
Tepelné ztráty výměníku (%) = |  |  |  | 0 | 0
VYPOČTENÉ HODNOTY
Médium 1 |  |  |  | pitná voda | pitná voda
Počet paralelních kanálů v 1 tahu |  |  | ppk1 (-) = | 3 | 2
Počet tahů zapojených v serii |  |  | pts1 (-) = | 11 | 7
Rychlost kapaliny |  |  | w1 (m/s) = | 0.227 | 0.3405
Součinitel přestupu tepla |  |  | alfa1 (W/m2*K) = | 11948.9419 | 12177.2445
Celkové tlakové ztráty sekce |  |  | dpz1c (kPa) = | 53.353 | 70.5844
Teplo předané ohř. médiu |  |  | Q1 (kW) = | 208.7523 | 208.1087
Médium 2 |  |  |  | invert.sirup | invert.sirup
Počet paralelních kanálů v 1 tahu |  |  | ppk2 (-) = | 6 | 2
Počet tahů zapojených v serii |  |  | pts2 (-) = | 6 | 7
Rychlost kapaliny |  |  | w2 (m/s) = | 0.14605 | 0.43815
Součinitel přestupu tepla |  |  | alfa2 (W/m2*K) = | 333.7454 | 912.9738
Celkové tlakové ztráty sekce |  |  | dpz2c (kPa) = | 26.4809 | 224.4313
Teplo odebrané ochl. médiu |  |  | Q2 (kW) = | 208.9646 | 208.6012
Součinitel prostupu tepla |  |  | k(W/m2*K) = | 310.8822 | 760.9721
Středni log. teplotní diference |  |  | dtlog (oC) = | 22.2692 | 22.3502
Celkový počet desek v sekci (výměníku) |  |  | nc (-) = | 70 | 29
Celk. teplosměnná plocha sekce (vým.) |  |  | Ac (m2) = | 30.153 | 12.236
Max. přípustný tlak ve vým. (sekci) |  |  | pmax (kPa) = | 1000 | 1000
Hmotnost desek v sekci (kg) |  |  |  | 378 | 156.6
Hmotnost sekce se stojanem (kg) |  |  |  | 578 | 356.6
Hmotnost kapalin v sekci (kg) |  |  |  | 164.7238 | 66.8444
Hmotnost plné sekce se stojanem(kg) |  |  |  | 742.7238 | 423.4444
M2 - sirup
M1 - chl. voda
t22
t21
t12
t11
M2 - sirup
M1 - chl. voda
t22
t21
t12
t11

## HE design
PLATE HEAT EXCHANGER CALCULATION
(drinking water - inverted sirup 75 % D.M.) | [5 empty] | t22 = ?
GIVEN DATA
Typ of HE: |  | CHS VT - 05
Section: | Production Lines - An example showing an effect of plates arrangement
to pressure loss and heat transfer areas for the same thermal capacity.
|  |  |  | 1.variant | 2.variant
Liquid 1 - heated: |  |  |  | drinking water | drinking water
- inlet temperature |  |  | t11 (oC) = | 15 | 15
- outlet temperature |  |  | t12 (oC) = | 60 | 60
(given value or for a max. HE capacity calculation |  |  |  | 59.989 | 59.8503
is estimated according results - see right)
- flow rate |  |  | M1 (kg/h) = | 4000 | 4000
- max. acceptable pressure loss |  |  | dp1max (kPa) = | 100 | 100
- fouling thickness |  |  | s1i (mm) = | 0 | 0
- fouling thermal conductivity |  |  | lambda1i (W/mK) = | 2 | 2
Liquid 2 - cooled: |  |  |  | invert.sirup | invert.sirup
- inlet temperature |  |  | t21 (oC) = | 80 | 80
- outlet temperature |  |  | t22 (oC) = | 40 | 40
(estimation for the 1st iteration - than set up according results) |  |  |  | 39.75 | 39.82
- flow rate |  |  | M2 (kg/h) = | 7000 | 7000
- max. acceptable pressure loss |  |  | dp2max (kPa) = | 100 | 250
- fouling thickness |  |  | s2i (mm) = | 0.1 | 0.1
- fouling thermal conductivity |  |  | lambda2i (W/mK) = | 2 | 2
Type of flows in HE: parallel flow / counter flow: |  |  |  | counter flow | counter flow
Note: |  | Effect of a number of parallel chanels and a number of passes
to overall heat transfer coefficient, pressure loss, heat transfer
surface (for the came HE capacity)
Var.1 - low pressure loss; var.2 - high pressure loss)
Performed by: |  | P. Hoffman
Date: |  | April 2003
CONSTANTS FOR CALCULATIONS
- space (gap) between plates |  |  | s (mm) = | 4 | 4
- channel width |  |  | b (mm) = | 410 | 410
- channel length |  |  | L (mm) = | 1240 | 1240
- equivalent diameter |  |  | de (m) = | 0.0079227 | 0.0079227
- channel clear area |  |  | f (m2) = | 0.00164 | 0.00164
- heat transfer area of 1 plate |  |  | A (m2) = | 0.437 | 0.437
- recommended velocities for water and similar solutions 0,3 - 0,6 m/s (for viscous is <)
(set velocities modify according calculated and acceptable pressure losses)
- medium 1: |  | water | w1rec (m/s) = | 0.4 | 0.4
- medium 2: |  | sirup | w2rec (m/s) = | 0.2 | 0.2
- physical properties calculation
(take them from tables - for water they are calculated automatically)
- max. acceptable pressure in channels |  |  | pmax (kPa) = | 1000 | 1000
- criteria equations for heat transfer coefficient and pressure loss specification
(take from literature etc. for given type of plates)
- plate thickness |  |  | sd (mm) = | 1.3 | 1.3
- plate thermal conductivity |  |  | lambdad (W/mK) = | 15 | 15
- plate mass |  |  | Md (kg) = | 5.4 | 5.4
- frame mass |  |  | Mst (kg) = | 200 | 200
(take for given type of HE)
- heat loss of HE |  |  | z (%) = | 0 | 0
(in % of transfered heat)
CALCULATIONS
1. Physical properties calculations
- Liquid 1: |  |  |  | drinking water | drinking water
- average temperature |  |  | t1s (oC) = | 37.5 | 37.5
- specific heat |  |  | c1 (kJ/kg.K) = | 4.1761 | 4.1761
- density |  |  | ro1 (kg/m3) = | 994.8571 | 994.8571
- thermal conductivity |  |  | lambda1 (W/m.K) = | 0.62404 | 0.62404
- dynamic viscosity |  |  | mi1 (Pa.s) = | 0.00068649 | 0.00068649
- kinematic viscosity |  |  | ni1 (m2/s) = | 6.9004e-07 | 6.9004e-07
- Prandtl number |  |  | Pr1 (-) = | 4.5229 | 4.5229
- Liquid 2 (for 1st iteration): |  |  |  | invert.sirup | invert.sirup
- average temperature |  |  | t2s (oC) = | 60 | 60
- specific heat |  |  | c2 (kJ/kg.K) = | 2.67 | 2.67
2. Thermal output
Q1 = M1*c1*(t12-t11)/3600 |  |  | Q1 (kW) = | 208.8034 | 208.8034
Q2 = 100*Q1/(100-z); Q2´=M2*c2*(t21-t22) |  |  | Q2 (kW) = | 208.8034 | 208.8034
t22 = t21-(t12-t11)*M1*c1/(M2*c2) |  |  | Q2´ (kW) = | 207.6667 | 207.6667
1. iteration | 60 | 4.1858 | t22 (oC) = | 54.3452 | 54.3452 | 60 | 4.1858
2. iteration | 67.1726 | 4.1898 | t22 (oC) = | 54.3701 | 54.3701 | 67.1726 | 4.1898
3. iteration | 67.185 | 4.1898 | t22 (oC) = | 54.3701 | 54.3701 | 67.185 | 4.1898
4. iteration | 67.1851 | 4.1898 | t22 (oC) = | 54.3701 | 54.3701 | 67.1851 | 4.1898
5. iteration | 67.1851 | 4.1898 | t22 (oC) = | 54.3701 | 54.3701 | 67.1851 | 4.1898
- Liquid 2 (for next calculations): |  |  |  | invert.sirup | invert.sirup
- average temperature |  |  | t2s (oC) = | 67.1851 | 67.1851
- specific heat |  |  | c2 (kJ/kg.K) = | 2.67 | 2.67
- density |  |  | ro2 (kg/m3) = | 1353 | 1353
- thermal conductivity |  |  | lambda2 (W/m.K) = | 0.391 | 0.391
- dynamic viscosity |  |  | mi2 (Pa.s) = | 0.025 | 0.025
- kinematic viscosity |  |  | ni2 (m2/s) = | 1.8477e-05 | 1.8477e-05
- Prandtl number |  |  | Pr2 (-) = | 170.7161 | 170.7161
3. Velocities of both liquids in interplate channels
velocity for a case that all liquid flows through 1 channel
w1c = M1/(3600*ro1*f) |  |  | w1c (m/s) = | 0.68101 | 0.68101
w2c = M2/(3600*ro2*f) |  |  | w2c (m/s) = | 0.8763 | 0.8763
number of parallel chanels in 1 pass - calculated from set wirec
npch1c = w1c/w1rec |  |  | npch1c (-) = | 1.7025 | 1.7025
npch2c = w2c/w2rec |  |  | npch2c (-) = | 4.3815 | 4.3815
select number of parallel channels in 1 pass
npch1 |  | drinking water | npch1 (-) = | 3 | 2
npch2 |  | invert.sirup | npch2 (-) = | 6 | 2
velocities in interplate channels
w1 = M1/(3600*ro1*f*npch1) |  |  | w1 (m/s) = | 0.227 | 0.3405
w2 = M2/(3600*ro2*f*npch2) |  |  | w2 (m/s) = | 0.14605 | 0.43815
4. Calculation of heat transfer and overall heat transfer coeffitients
Re1 = w1*de/ni1 |  |  | Re1 (-) = | 2606.3266 | 3909.4898
Nu1 = 0,0206*(Re1^0.916)*(Pr1^0.40)
|  |  | Nu1 (-) = | 50.7128 | 73.5219
alfa1 = Nu1*lambda1/de
|  |  | alfa1 (W/m2*K) = | 3994.4572 | 5791.0507
Re2 = w2*de/ni2 |  |  | Re2 (-) = | 62.623 | 187.869
Nu2 = 0,0206*(Re2^0.916)*(Pr2^0.40)
|  |  | Nu2 (-) = | 7.1217 | 19.4818
alfa2 = Nu2*lambda2/de
|  |  | alfa2 (W/m2*K) = | 351.4702 | 961.4609
k = 1/(1/alfa1+sd/lambdad+si1*0.001/lambdai1+si2*0.001/lambdai2+1/alfa2)
|  |  | k (W/m2*K) = | 309.3864 | 741.0532
5. Calculation of number of plates in HE
dtlog = abs((t22-t11)-(t21-t12))/ln(abs((t22-t11)/(t21-t12)))
|  |  | dtlog (oC) = | 28.6001 | 28.6001
calculated total heat transfer area
Aco = Q1*1000/(k*dtlog) |  |  | Aco (m2) = | 23.5977 | 9.8519
calculated number of plates
nco = Aco/A1 |  |  | nco (-) = | 53.9993 | 22.5445
calculated number of passes in series (every pass with npchi parallel channels)
nps1c = nco/(2*npch1) |  |  | nps1c (-) = | 8.9999 | 5.6361
nps2c = nco/(2*npch2) |  |  | nps2c (-) = | 4.4999 | 5.6361
selected number of passes in series
nps1 = nco/(2*npch1) |  |  | nps1 (-) = | 11 | 7
nps2 = nco/(2*npch2) |  |  | nps2 (-) = | 6 | 7
check of correctness of selected numbers of parallel channels and passes in series. Difference between
numbers of plates npl1 and npl2 can be max. 2 (outside plates/channels), else some passes have to have
less or more channels (e.g. instead 6 x 6 = 36 would be 3 x 6 + 3 x 5 = 33)
|  |  | npl1 (-) = | 33 | 14
|  |  | npl2 (-) = | 36 | 14
Total number of plates in HE
npl = nps1*npch1+nps2*npch2+1 = npl1+npl2+1 |  |  | npl (-) = | 70 | 29
Total heat transfer area of HE
At = (npl-1)*A1 |  |  | At (m2) = | 30.153 | 12.236
6. Pressure loss check-up
Liquid 1 |  |  |  | drinking water | drinking water
Eu1 = 486*(Re1^-0.195)*(Pr1^-0.068)
|  |  | Eu1 (-) = | 94.6111 | 87.4187
pressure loss in 1 channel
Dp11 = Eu1*ro1*w1^2/1000 |  |  | Dp11 (kPa) = | 4.8503 | 10.0835
total pressure loss in HE
Dp1t = nps1*Dp11 |  |  | Dp1t (kPa) = | 53.353 | 70.5844
max. acceptable pressure loss |  |  | Dp1max = | 100 | 100
Liquid 2 |  |  |  | invert.sirup | invert.sirup
Eu2 = 486*(Re2^-0.195)*(Pr2^-0.068)
|  |  | Eu2 (-) = | 152.925 | 123.4354
pressure loss in 1 channel
Dp21 = Eu2*ro2*w2^2/1000 |  |  | Dp21 (kPa) = | 4.4135 | 32.0616
total pressure loss in HE
Dp2t = nps2*Dp21 |  |  | Dp2t (kPa) = | 26.4809 | 224.4313
max. acceptable pressure loss |  |  | Dp2max = | 100 | 250
max. acceptable pressure in HE |  |  | pmax (kPa) = | 1000 | 1000
If pressure losses are considerably different from acceptable ones it is necessary to select
another number of parallel channels and all calculations repeat (see below).
NEW CALCULATIONS - specifiation of max. performance of the specified HE
selected number of parallel channels in 1 pass
npch1 |  | drinking water | npch1 (-) = | 3 | 2
npch2 |  | invert.sirup | npch2 (-) = | 6 | 2
flow velocities in channels
w1 = M1/(3600*ro1*f*npch1) |  |  | w1 (m/s) = | 0.227 | 0.3405
w2 = M2/(3600*ro2*f*npch2) |  |  | w2 (m/s) = | 0.14605 | 0.43815
selected number of passes in series
nps1 = nco/(2*npch1) |  |  | nps1 (-) = | 11 | 7
nps2 = nco/(2*npch2) |  |  | nps2 (-) = | 6 | 7
check of correctness of selected numbers of parallel channels and passes in series. Difference between
numbers of plates npl1 and npl2 can be max. 2 (outside plates/channels), else some passes have to have
less or more channels (e.g. instead 6 x 6 = 36 would be 3 x 6 + 3 x 5 = 33)
|  |  | npl1 (-) = | 33 | 14
|  |  | npl2 (-) = | 36 | 14
Total number of plates in HE
npl = nps1*npch1+nps2*npch2+1 = npl1+npl2+1 |  |  | npl (-) = | 70 | 29
Total heat transfer area of HE
At = (npl-1)*A1 |  |  | At (m2) = | 30.153 | 12.236
Calculation of overall heat transfer coefficient
Re1 = w1*de/ni1 |  |  | Re1 (-) = | 2606.3266 | 3909.4898
Nu1 = 0,0206*(Re1^0.916)*(Pr1^0.40)
|  |  | Nu1 (-) = | 151.7011 | 154.5996
alfa1 = Nu1*lambda1/de
|  |  | alfa1 (W/m2*K) = | 11948.9419 | 12177.2445
Re2 = w2*de/ni2 |  |  | Re2 (-) = | 62.623 | 187.869
Nu2 = 0,0206*(Re2^0.916)*(Pr2^0.40)
|  |  | Nu2 (-) = | 6.7626 | 18.4993
alfa2 = Nu2*lambda2/de
|  |  | alfa2 (W/m2*K) = | 333.7454 | 912.9738
k = 1/(1/alfa1+sd/lambdad+si1*0.001/lambdai1+si2*0.001/lambdai2+1/alfa2)
|  |  | k (W/m2*K) = | 310.8822 | 760.9721
Calc. of a max. cooling down of liquid 2 and max. heating up of liquid 1 in the HE
estimation of t22 pro i- iter. - inv. sirup |  |  | t22i (°C) = | 39.75 | 39.82
calculated value t22 from i+1 iter. |  |  | t22i+1 (°C) = | 39.7909 | 39.9149
estimation of t12 for i- iter. - d. water |  |  | t12i (°C) = | 60.04 | 59.95
calculated value t12 from i+1 iter. |  |  | t12i+1 (°C) = | 59.989 | 59.8503
dtlog = abs((t22i-t11)-(t21-t12i))/ln(abs((t22i-t11)/(t21-t12i)))
|  |  | dtlog (oC) = | 22.2692 | 22.3502
Max. amount of transfered heat in the HE
Qmax=k*Ac*dtlog |  |  | Qmax (kW) = | 208.7523 | 208.1087
Check-up of heat given to cooling water and taken away from cooled sirup
Q1 = M1*c1*(t12i-t11)/3600 |  |  | Q1 (kW) = | 208.7523 | 208.1087
Q2 = 100*Q1/(100-z) |  |  | Q2 (kW) = | 208.7523 | 208.1087
Q2´=M2*c2*(t21-t22i) |  |  | Q2´ (kW) = | 208.9646 | 208.6012
Temperature of cooled liquid 1 |  |  | t22i+1 (°C) = | 39.7909 | 39.9149
Temperature of heated liquid 2 |  |  | t12i+1 (°C) = | 59.989 | 59.8503
Pressure loss check-up
Liquid 1
Eu1 = 486*(Re1^-0.195)*(Pr1^-0.068)
|  |  | Eu2 (-) = | 94.6111 | 87.4187
pressure loss in 1 channel
Dp11 = Eu1*ro1*w1^2/1000 |  |  | Dp11 (kPa) = | 4.8503 | 10.0835
total pressure loss in HE
Dp1t = nps1*Dp11 |  |  | Dp1t (kPa) = | 53.353 | 70.5844
Liquid 2
Eu2 = 486*(Re2^-0.195)*(Pr2^-0.068)
|  |  | Eu2 (-) = | 152.925 | 123.4354
pressure loss in 1 channel
Dp21 = Eu2*ro2*w2^2/1000 |  |  | Dp21 (kPa) = | 4.4135 | 32.0616
total pressure loss in HE
Dp2t = nps2*Dp21 |  |  | Dp2t (kPa) = | 26.4809 | 224.4313
comparison of calculated and acceptable pressure losses
max. acceptable pressure loss
|  |  | Dp1max (kPa)= | 100 | 100
|  |  | Dp2max (kPa)= | 100 | 250
max. acceptable pressure in HE
|  |  | pmax (kPa) = | 1000 | 1000
If pressure losses are considerably different from acceptable ones it is necessary to select
another number of parallel channels and all calculations repeat (see above).
If results are satisfactory you can print results of calculations
Print of results
PLATE HEAT EXCHANGER CALCULATION
t22 = ?
GIVEN DATA
Typ of HE: |  | CHS VT - 05
Section: | Production Lines - An example showing an effect of plates arrangement
to pressure loss and heat transfer areas for the same thermal capacity.
Note: |  | Effect of a number of parallel chanels and a number of passes
to overall heat transfer coefficient, pressure loss, heat transfer
surface (for the came HE capacity)
Var.1 - low pressure loss; var.2 - high pressure loss)
Performed by: |  | P. Hoffman
Date: |  | April 2003
|  |  |  | 1.variant | 2.variant
Type of flows in HE: |  |  |  | counter flow | counter flow
Liquid 1 - heated: |  |  |  | drinking water | drinking water
- inlet temperature |  |  | t11 (oC) = | 15 | 15
- calculated outlet temperature |  |  | t12 (oC) = | 59.989 | 59.8503
- flow rate |  |  | M1 (kg/h) = | 4000 | 4000
- max. acceptable pressure loss |  |  | Dp1max (kPa)= | 100 | 100
- fouling thickness |  |  | s1i (mm) = | 0 | 0
- fouling thermal conductivity |  |  | lambda1i (W/mK) = | 2 | 2
Liquid 2 - cooled: |  |  |  | invert.sirup | invert.sirup
- inlet temperature |  |  | t21 (oC) = | 80 | 80
- calculated outlet temperature |  |  | t22 (oC) = | 39.7909 | 39.9149
- flow rate |  |  | M2 (kg/h) = | 7000 | 7000
- max. acceptable pressure loss |  |  | Dp2max (kPa)= | 100 | 250
- fouling thickness |  |  | s2i (mm) = | 0.1 | 0.1
- fouling thermal conductivity |  |  | lambda2i (W/mK) = | 2 | 2
- heat loss of HE |  |  | HL (%) = | 0 | 0
(in % of transfered heat)
CALCULATED DATA
Liquid 1 |  |  |  | drinking water | drinking water
Number of parallel channels in 1 pass |  |  | npch1 (-) = | 3 | 2
Number of passes in series |  |  | nps1 (-) = | 11 | 7
Flow velocity in channels |  |  | w1 (m/s) = | 0.227 | 0.3405
Heat transfer coefficient |  |  | alfa1 (W/m2*K) = | 11948.9419 | 12177.2445
Total pressure loss in HE |  |  | Dp1t (kPa) = | 53.353 | 70.5844
Heat given to heated liquid |  |  | Q1 (kW) = | 208.7523 | 208.1087
Liquid 2 |  |  |  | invert.sirup | invert.sirup
Number of parallel channels in 1 pass |  |  | npch2 (-) = | 6 | 2
Number of passes in series |  |  | nps2 (-) = | 6 | 7
Flow velocity in channels |  |  | w2 (m/s) = | 0.14605 | 0.43815
Heat transfer coefficient |  |  | alfa2 (W/m2*K) = | 333.7454 | 912.9738
Total pressure loss in HE |  |  | Dp2t (kPa) = | 26.4809 | 224.4313
Heat given to cooled liquid |  |  | Q2 (kW) = | 208.9646 | 208.6012
Overall heat transfer coefficient |  |  | k(W/m2*K) = | 310.8822 | 760.9721
Log. meat temperature difference |  |  | Dtlog (oC) = | 22.2692 | 22.3502
Total number of plates in HE |  |  | npl (-) = | 70 | 29
Total heat transfer area of HE |  |  | At (m2) = | 30.153 | 12.236
Max. acceptable pressure in HE |  |  | pmax (kPa) = | 1000 | 1000
Mass of plates in HE |  |  | mpl (kg) = | 378 | 156.6
Mass of HE (plates + frame) |  |  | mHE (kg) = | 578 | 356.6
Mass of both liquids in HE |  |  | mliq (kg) = | 164.7238 | 66.8444
Total working mass of HE |  |  | mHEt (kg) = | 742.7238 | 423.4444
M2 - sirup
M1 - cooling water
t22
t21
t12
t11
M2 - sirup
M1 - cooling water
t22
t21
t12
t11